## AVR spec for Vendor
Technical Specification of AVR:
S/N | Items | Specification | Marking severity | Vendor technical feedback as per OEM | Comments
1 | Product | Automatic Voltage Regulator (AVR) | Info
2 | AVR type | Servo Type | Mandatory
3 | Brand | Need to mention | Critical
4 | Country of Origin | Europe/USA/Australia | Critical
5 | Rated Capacity (KVA) | 60/100/120/320/400/1000/1600/2000 | Critical
6 | Phase | Three Phase | Mandatory
7 | Connection type | Three phase Four wires | Mandatory
8 | Voltage Stabilisation | Independent phase Control | Critical
INPUT
9 | Input Lower cut-off voltage | 320 VAC (Line to Line) | High Critical
10 | Input higher cut-off voltage | 460 VAC (Line to Line) | High Critical
11 | Input Frequency | 50Hz ± 5% | Critical
12 | Input Connection | Vendor need to mention | Major
13 | Regulation Voltage Range | -20%/+15% | Major
14 | Operating Voltage Range | Vendor need to mention | Major
OUTPUT
15 | Voltage | 400 VAC Three Phase (Line to Line) | Critical
16 | Voltage Tolerance | ± 0.5% | Critical
17 | Output Frequency | 50 Hz ± 1% | Critical
18 | Current | Vendor need to mention | Major
19 | Overload Capability (mention the time in respect of % loading) | 110% 130% 150% 200% | Critical
20 | Correction time | 12 ms/V to 22ms/V ( as per capacity) | Critical
21 | Correction Speed | 500 V/sec (Optional full regulation up to 3 cycles) or as per OEM | Major
22 | Output Connection | 1000 KVA+ is ACB and Less than 1000 KVA is MCCB (AVR o/p will connect with exisitng AVR bypass DB) | Mandatory
23 | LCD Display | -Input Voltage Value (Three Phases, between phase and neutral) -Output Voltage Value (Three Phases, between phase and neutral) -Output Load Percentage /each phase -Output Frequency -Stabilizer Condition and Failure Info -Warnings (Overload, over temperature, input failure, output failure, etc) -harmonics are requied | Critical
24 | Communication | Though a software support and “Remote Management System”(Via Network) or SNMP based, the ability of monitoring and Management Optional or as per OEM | Critical
PROTECTION
25 | Input Voltage Protection | Stabilizer shut off electronically under / over voltage | Critical
26 | Output Voltage Protection | Stabilizer shut off electronically under / over voltage | Critical
27 | Input Current Protection | ACB with motor or as per OEM | Critical
28 | Output Current Protection | ACB with motor (Optional) or as per OEM | Critical
29 | Over Temperature Protection | Stabilizer shut off for over - temperature | Critical
30 | Manual By-pass Switch | I-0-II position Manual By-pass switch for failure and Maintenance (Through ACB), Auto Bypass and Manual bypass | Major
31 | Surge Arrester | Suitable Surge Filter unit for lightning and high voltage | Major
ENVERONMENT
32 | Operating Temperature | 0 °C ~ +50 °C | Critical
33 | Storage Temperature | 0 °C ~ +50 °C | Critical
34 | Altitude | < 4000m | Minor
35 | Humidity | 95% or as per OEM | Critical
36 | Acoustic Noise | At least < 60 dB @1m | Critical
CONSTRUCTION
37 | Type | Indoor | Minor
38 | Protection Class | IP 21/ IP22 | Critical
39 | Color | RAL 7035 | Minor
40 | Base | Both Strong Wheel and Nut Bolt | Minor
41 | Cooling | Natural Air Ventilation | Critical
42 | Dimensions (WxDxH) | Maximum allowable dimension is although we are expecting as low as possible) 2000KVA: 4800 W x 1400 D x 2200 H mm 1600KVA: 4800 W x 1000 D x 2100 H mm 1000KVA: 4200 W x 1000 D x 2000 H mm 400KVA: 1800 W x 800 D x 2000 H mm 320KVA: 1600 W x 800 D x 1800 H mm 120KVA: 1200 W x 800 D x 2000 H mm 100KVA: 1000 W x 800 D x 1800 H mm 60KVA: 1000 W x 800 D x 1800 H mm | Critical
43 | Weight | Vendor need to mention | Major
44 | Coil | Phase wise Indipendent Transformer coil | Critical
Others
45 | Motor | AC Motor | Minor
46 | Load Power Factor | Minimum 96%, need mention by Vendor | Critical
47 | Harmonic distortion | < 1% (please share the details mechanism) | Critical
48 | Waveform distortion | Negligible | Minor
49 | Initial Resistance | < 2 Ohm | Minor
50 | Phase controlling type/phase correction methotology | Vendor need to mention | Minor
51 | Control system | Vendor need to mention | Minor
52 | Correction speed | Vendor need to mention | Minor
53 | Transient Suppression | <1000 V peak | Major
54 | Wave Form Distortion | Nil | Minor
55 | Load power Factor Effect | Nil | Minor
56 | LED indicator | Normal, High Volt, Low Volt, Delay,Trip | Major
57 | Input / Output Volt meter | 0 ~ 500 Volt (Brand: Schneider/ABB) | Minor
58 | Amps meter | 0 ~ 3000 Amps/ depend on capacity (Brand: Schneider/ABB) | Minor
59 | External Alarm | Vendor need to mention | Major
60 | Output Voltage Indication | By 01 No Digital Voltmeter With Selector switch (Brand: Schneider/ABB) | Minor
61 | Output Amper Indication | By 03 No Digital Ammeter (Brand: Schneider/ABB) | Minor
62 | Connecting Busbar and Transformer coil | 100% Pure Copper | Critical
63 | Trip and Restart | Through output breaker (please share the details) | Critical
64 | Circuit Breaker | Capacity depend on AVR capacity, Vendor need to mention, (Brand: Schneider/ABB) | Major
65 | Speed of Response | 12 ms/V to 22ms/V as per capacity | Critical
66 | Efficiency | 98% or Vendor need to mentioned | Critical
67 | Duty cycle | 110% Continues or vendor need to mentioned | Major
68 | Protection | High and Low Voltage with restart, Surge, Surge absorver, Spike, Delay time for Voltage Fluctuation, Phase failure protection. Over Load and Short Circuit (by Air-circuit breaker), Phase sequence mismatch, Power factor protection, (Brand: Schneider/ABB) | Major
69 | Cable Entrance | As per Standard | Minor
70 | Earthling Point | Separate | Minor
71 | Connection diagram | Include with system | Minor
72 | User manual | Include with system | Minor
73 | Warranty and Guaranty | Minimum 2 years | Mandatory
74 | Spare parts availability | Minimum 10 years | Critical
75 | Life time | 15 Years | Critical
76 | 3 phase Power Analyzer | It must show KW, KVA, PF, AMP, Voltage for single and three phase | Minor
77 | Monitoring Protocol | SNMP/BACnet/Modbus | Critical
78 | Protocol Version | Vendor need to mention the protocol version like V2, V3 etc. | Critical
79 | Protocol file | Need to share the protocol file | Critical
80 | Cooling Type | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring | Critical