## Spec of Displacement PCU
Technical Specification of Precision Air Conditioner
S/N | Specifications
S/N | Specifications for Displacement Cooling |  |  | Vendor feedback as per OEM specification
|  | Importance | Remarks/Notes | 4 TON Displacement PCU | 6 TON Displacement PCU | 8 TON Displacement PCU | 10 TON Displacement PCU
1 | Product Brand (Need to mention by supplier) | High Critical | Please mention the brand name
2 | Country of Origin (UK/USA/Germany/Italy/France/Japan) | High Critical | Please mention the country
3 | Product Manufacturing Country (UK/USA/Germany/Italy/France/Japan) | High Critical | Please mention the country
4 | Product Shipment From | Critical | Please mention the country
5 | Product Model | Info | Mention the model name
6 | Product Standard: ISO 14001:2015, ISO 9001:2015 or better | Critical | Please mention the standard name
7 | End of Support (EoS) of the Precision Air Conditioner | Critical | Mention in year
8 | End of Life (EoL) of the Precision Air Conditioner | Critical | Mention in year
9 | Gross Cooling Capacity (KW) | High Critical | Mention in KW
10 | Gross Sensible Cooling Capacity (KW) | High Critical | Mention in KW
11 | Net/performance total Coolling capacity (KW) | High Critical | Mention in KW
12 | Net/performance sensible cooling capacity (KW) | Critical | Mention in KW
13 | Latent capacity (humid.) (KW) | Major | Mention in KW
14 | Condensing temperature: 45 °C to 50 °C | Critical
15 | EER (Energy Efficiency Ratio) (W/W) | Critical
16 | SHR (Sensible Heat Ratio) (W/W) | Critical
17 | Sound power level (Dba) | Critical | Mention in dBA
18 | Number of refrigerant circuits | Major | Please mention
19 | Total power consumption (KW) | Critical | Mention in KW
20 | Airflow (m3/h) | High Critical
21 | Return air temperature: 25°C to 30 °C | Critical
22 | Return Air humidity: 50% rel | Critical
23 | Supply air temperature: 20 °C to 24 °C | Critical
24 | Dimention: (HxWxD)mm Indoor | Major | Mention in mm
25 | Dimention: (HxWxD)mm Outdoor | Major | Mention in mm
26 | Weight indoor (KG) | Critical | Mention in KG
27 | Refrigerant: R410A or environment friendly agent | Critical
28 | Power supply: 400/3+N+PE/50 | Mandatory
29 | ESP external static pressure: 0 Pa | Major
30 | Motor-efficiency (%) | Major
31 | Filter Type (G4 or Coarse) | Major | Please mention
Compressor
1 | Compressor Type | Major | Please mention
2 | Electrical power consumption (KW) | Critical | Mention in KW
3 | Heat rejection Capacity (Kw) | Critical | Mention in KW
4 | Number of compressors | Major | Please mention
5 | Evaporating temperature | Major | Please mention in Degree Celsius
Condenser:
1 | Unit type/Model | Major | Please mention
2 | Ambient Temperature | Critical | Please mention in Degree Celsius
3 | Available Condenser Capacity | Critical | Mention in KW
4 | Number of Fans | Critical | Please mention the fan quantity
5 | Number of condensers | Major | Please mention the quantity
6 | Condenser weight (KG) | Major | Mention in KG
7 | Current consumption (A) | Major
8 | Power consumption KW | Critical | Mention in KW
9 | Dimention: (HxWxD)mm | Major | Mention in mm
10 | Airflow (m3/h) | Critical
11 | Air flow direction (90˚/180˚/270˚/360˚) | Critical | Please mention in Degree
12 | Cooling-air mixing ration (g/kg) | Major | Please mention the value
13 | Dew point (constant pressure & constant water vapor content) | Major | Please mention in Degree Celsius
14 | Wet bulb temperature | Major | Please mention in Degree Celsius
15 | Sufficient space (Vertical) for air diffuser | Major | Please mention in Centimeter
16 | Sufficient space for return air | Major | Please mention in Centimeter
17 | Output/Supply air temperature | Critical | Please mention in Degree Celsius
18 | Reurned air temperature range for working | Critical | Please mention in Degree Celsius
19 | Warranty of the full product (Minimum 2 Years) | High Critical | Mention in year
20 | Installation & Commissioning of each Cooling system | Critical | Mention in week
21 | Air flow type | Critical | Horizontal
22 | Monitoring Protocol | Critical | SNMP/BACnet/Modbus
23 | Protocol Version | Critical | Vendor need to mention the protocol version like V2, V3 etc.
24 | Protocol file | Critical | Need to share the protocol file
25 | Cooling Type | Critical | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring

## Spec of In-Row PCU
Technical Specification of Precision Air Conditioner
S/N | Specifications
S/N | Specifications for in-Row Cooling |  | Remarks/Notes | Vendor feedback as per OEM specification
|  | Importance |  | 6 TON in-row PCU | 8 TON in-row PCU | 10 TON in-row PCU
1 | Product Brand (Need to mention by supplier) | High Critical | Please mention the brand name
2 | Country of Origin (UK/USA/Germany/Italy/France/Japan) | High Critical | Please mention the country
3 | Product Manufacturing Country (UK/USA/Germany/Italy/France/Japan) | High Critical | Please mention the country
4 | Product Shipment From | Critical | Please mention the country
5 | Product Model | Info | Mention the model name
6 | Product Standard: ISO 14001:2015, ISO 9001:2015 or better | Critical | Please mention the standard name
7 | End of Support (EoS) of the Precision Air Conditioner | Critical | Mention in year
8 | End of Life (EoL) of the Precision Air Conditioner | Critical | Mention in year
9 | Gross Cooling Capacity (KW) | High Critical | Mention in KW
10 | Gross Sensible Cooling Capacity (KW) | High Critical | Mention in KW
11 | Net/performance total Coolling capacity (KW) | High Critical | Mention in KW
12 | Net/performance sensible cooling capacity (KW) | Critical | Mention in KW
13 | Latent capacity (humid.) (KW) | Major | Mention in KW
14 | Condensing temperature: 45 °C to 50 °C | Critical
15 | EER (Energy Efficiency Ratio) (W/W) | Critical
16 | SHR (Sensible Heat Ratio) (W/W) | Critical
17 | Sound power level (Dba) | Critical | Mention in dBA
18 | Number of refrigerant circuits | Major | Please mention
19 | Total power consumption (KW) | Critical | Mention in KW
20 | Airflow (m3/h) | High Critical
21 | Return air temperature: 25°C to 30 °C | Critical
22 | Return Air humidity: 50% rel | Critical
23 | Supply air temperature: 20 °C to 24 °C | Critical
24 | Dimention: (HxWxD)mm Indoor | Major | Mention in mm
25 | Dimention: (HxWxD)mm Outdoor | Major | Mention in mm
26 | Weight indoor (KG) | Critical | Mention in KG
27 | Refrigerant: R410A or environment friendly agent | Critical
28 | Power supply: 400/3+N+PE/50 | Mandatory
29 | ESP external static pressure: 0 Pa | Major
30 | Motor-efficiency (%) | Major
31 | Filter Type (G4 or Coarse) | Major | Please mention
Compressor
1 | Compressor Type | Major | Please mention
2 | Electrical power consumption (KW) | Critical | Mention in KW
3 | Heat rejection Capacity (Kw) | Critical | Mention in KW
4 | Number of compressors | Major | Please mention
5 | Evaporating temperature | Major | Please mention in Degree Celsius
Condenser:
1 | Unit type/Model | Major | Please mention
2 | Ambient Temperature | Critical | Please mention in Degree Celsius
3 | Available Condenser Capacity | Critical | Mention in KW
4 | Number of Fans | Critical | Please mention the fan quantity
5 | Number of condensers | Major | Please mention the quantity
6 | Condenser weight (KG) | Major | Mention in KG
7 | Current consumption (A) | Major
8 | Power consumption KW | Critical | Mention in KW
9 | Dimention: (HxWxD)mm | Major | Mention in mm
10 | Airflow (m3/h) | Critical
11 | Air flow direction (90˚/180˚/270˚/360˚) | Critical | Please mention in Degree
12 | Cooling-air mixing ration (g/kg) | Major | Please mention the value
13 | Dew point (constant pressure & constant water vapor content) | Major | Please mention in Degree Celsius
14 | Wet bulb temperature | Major | Please mention in Degree Celsius
15 | Sufficient space (Vertical) for air diffuser | Major | Please mention in Centimeter
16 | Sufficient space for return air | Major | Please mention in Centimeter
17 | Output/Supply air temperature | Critical | Please mention in Degree Celsius
18 | Reurned air temperature range for working | Critical | Please mention in Degree Celsius
19 | Warranty of the full product (Minimum 2 Years) | High Critical | Mention in year
20 | Installation & Commissioning of each Cooling system | Critical | Mention in week
21 | Monitoring Protocol | Critical | SNMP/BACnet/Modbus
22 | Protocol Version | Critical | Vendor need to mention the protocol version like V2, V3 etc.
23 | Protocol file | Critical | Need to share the protocol file
24 | Cooling Type | Critical | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring

## Comfort AC_Wall Mounted
Technical Specification of Comfort AC
Vendor feedback as per OEM specification
S/N | Specification | Description/Requirement | Unit | Example | Importance | 2 Ton split AC | 3 Ton split AC | 5 Ton split AC | Remarks/Notes
1 | Type | Wall/Ceiling Mounted |  |  | Mandatory
2 | Brand name | General/Daikin/Hitachi/Carrier/Similar |  | General | High Critical
3 | Country of origin | Please mention the country name |  | Japan | Critical
4 | Capacity | Cooling | BTU/Hr | 36000 | Major
|  | Compressor | Type | Reciprocatory | Major
5 | Electricity Rating | Power Supply | Volt/Ph/Hz | 380-415/Three/50 | Critical
|  | Power Input | Watts | 3300 | Major
|  | Running Current | Amps | 6/PHASE | Critical
6 | Performance | EER | BTU/Hr./W | 10.91 | Major
|  | Airflow speed Indoor | CFM | 530 | Critical
|  | Airflow speed Outdoor | CFM | 159 | Critical
|  | Output air temperature | Celsius | 35 | Critical
|  | Moisture Removal | Lt/hr | 5 | Major
|  | Noise Level Indoor | db | 46 | Major
|  | Noise Level Outdoor | db | 59 | Major
7 | Operation | Panel Display | Type | LCD | Critical
|  | Remote Controller | Type | LCD | Critical
8 | Features | Temp. Control |  | Thermistor | Critical
|  | Air Direction |  | 4 Way Deflection | Major
|  | Energy Saver |  |  | Critical
|  | Auto Air Swing | Two Way |  | Major
|  | Speed Setting | Cooling/Fan | Top | Major
|  | Air Discharge |  |  | Major
|  | Auto Restart |  |  | Critical
|  | Dehumidification |  |  | Critical
|  | On/Off Timer |  |  | Major
9 | Filters | Anti-Bacteria Filter |  |  | Major
10 | Indoor | Dimension (Width x Height x Depth) | mm |  | Major
|  | Net Weight/Gross Weight | Kg |  | Major
11 | Outdoor | Dimension (Width x Height x Depth) | mm |  | Major
|  | Net Weight/Gross Weight | Kg |  | Major
12 | Warranty | Minimum 2 Years |  |  | High Critical
13 | Operationl Data | End of Support (EoS) | Year |  | Critical
|  | End of Life (EoL) | Year |  | High Critical
|  | Display parameters |  |  | Major
|  | Power Consumption | KW |  | Critical
14 | Delivery lead time from PO |  | Week |  | High Critical
15 | Installation & Commissioning of Cooling system |  | Week |  | Critical
16 | Monitoring Protocol | SNMP/BACnet/Modbus
17 | Protocol Version | Vendor need to mention the protocol version like V2, V3 etc.
18 | Protocol file | Need to share the protocol file
19 | Cooling Type | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring

## Comfort AC_Floor Standing
Technical Specification of Comfort AC
Vendor feedback as per OEM specification
S/N | Specification | Description/Requirement | Unit | Example | Importance | 3 Ton split AC | 5 Ton split AC | Remarks/Notes
1 | Type | Floor Standing |  |  | Mandatory
2 | Brand name | General/Daikin/Hitachi/Carrier/Similar |  | General | High Critical |  |  | Please mention
3 | Country of origin | Please mention the country name |  | Japan | Critical |  |  | Please mention
4 | Capacity | Cooling | BTU/Hr | 36000 | Major |  |  | Please mention
|  | Compressor | Type | Reciprocatory | Major
5 | Electricity Rating | Power Supply | Volt/Ph/Hz | 380-415/Three/50 | Critical |  |  | Please mention
|  | Power Input | Watts | 3300 | Major |  |  | Please mention
|  | Running Current | Amps | 6/PHASE | Critical |  |  | Please mention
6 | Performance | EER | BTU/Hr./W | 10.91 | Major |  |  | Please mention
|  | Airflow speed Indoor | CFM | 530 | Critical |  |  | Please mention
|  | Airflow speed Outdoor | CFM | 159 | Critical |  |  | Please mention
|  | Output air temperature | Celsius | 35 | Critical |  |  | Please mention
|  | Moisture Removal | Lt/hr | 5 | Major |  |  | Please mention
|  | Noise Level Indoor | db | 46 | Major |  |  | Please mention
|  | Noise Level Outdoor | db | 59 | Major |  |  | Please mention
7 | Operation | Panel Display | Type | LCD | Critical
|  | Remote Controller | Type | LCD | Critical
8 | Features | Temp. Control |  | Thermistor | Critical
|  | Air Direction |  | 4 Way Deflection | Major
|  | Energy Saver |  |  | Critical
|  | Auto Air Swing | Two Way |  | Major
|  | Speed Setting | Cooling/Fan | Top | Major
|  | Air Discharge |  |  | Major
|  | Auto Restart |  |  | Critical
|  | Dehumidification |  |  | Critical
|  | On/Off Timer |  |  | Major
9 | Filters | Anti-Bacteria Filter |  |  | Major
10 | Indoor | Dimension (Width x Height x Depth) | mm |  | Major
|  | Net Weight/Gross Weight | Kg |  | Major
11 | Outdoor | Dimension (Width x Height x Depth) | mm |  | Major
|  | Net Weight/Gross Weight | Kg |  | Major
12 | Warranty | Minimum 2 Years |  |  | High Critical
13 | Operationl Data | End of Support (EoS) | Year |  | Critical
|  | End of Life (EoL) | Year |  | High Critical
|  | Display parameters |  |  | Major
|  | Power Consumption | KW |  | Critical
14 | Delivery lead time from PO |  |  |  | High Critical
15 | Installation & Commissioning of Cooling system |  |  |  | Critical
16 | Monitoring Protocol | SNMP/BACnet/Modbus
17 | Protocol Version | Vendor need to mention the protocol version like V2, V3 etc.
18 | Protocol file | Need to share the protocol file
19 | Cooling Type | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring