## SOTC
Prime Generator Technical specification: 50KVA, 100KVA, 500KVA, 635KVA, 1000KVA
SL | Particulars | Specification | Marking severity | Vendor must provide feedback as per provided OEM catalogue | Vendor must provide feedback as per provided OEM catalogue | Vendor must provide feedback as per provided OEM catalogue | Vendor must provide feedback as per provided OEM catalogue | Vendor must provide feedback as per provided OEM catalogue | Vendor Remarks (if any) | Robi Remarks
| Capacity |  |  | 1000KVA | 700KVA | 500KVA | 100KVA | 60KVA
A | Standards
| Standards | ISO 8528 -1,2,3 & ISO 3046 or updated | Critical
B | Product data (Generator)
| Generator Brand | Cummins/ Tempest/ Caterpillar/Kohler/Bruno/F.G. Wilson or Equivalent | Critical
| Brand origin country | UK/USA/Germany/Italy/France | Mandatory
| Manufacturer & Assemble country | UK/USA/ Germany/Italy/ France/ China/India/EU | Critical
| Generator Model | Vendor must mention as per OEM catalogue | Info
| Shipment from | Vendor must mention | Critical
| High Capacity Generator (Prime): 50KVA, 100KVA, 500KVA, 635KVA, 1000KVA | Vendor must mention as per OEM catalogue | Mandatory
C | Engine Data
| Brand high capacity DG | Cummins/ Perkins/ Tempest/ Caterpillar or Equivalent | Critical
| Manufacturer & Assemble: | UK/USA/ Germany/Italy/ France/ China/India/EU | Critical
| Engine manufacturing year | Manufacturing year has to be recent year | Critical
| Country of origin: | UK/ USA/ Germany/Italy/ France | Mandatory
| Model: | Vendor must mention as per OEM catalogue | Info
| Type | Vertical, 4-stroke, compression ignition/as per OEM | Critical | [6 empty] | High Capacity DG Should V- Type
| No of Cylinder and Cylinder arrangement | Vendor must mention as per OEM catalogue | Major
| Capacity: Engine Power | Vendor must mention as per OEM catalogue | Critical
| Compression Ration | Vendor must mention as per OEM catalogue | Critical
| Cooling type/System | Water Cooled | Critical
| Speed/Engine RPM | 1500 RPM | Critical
| Engine | EC Controlled, heavy duty industrial type 4 stroke engine | Critical
| Engine Governing System | The Generator must be equipped with Electronic governor system | Critical
| Starting System | DC 12V / 24V Electric Start | Critical
| Rediator water tank capacity | Vendor will mention the capacity of proposed industrial type radiator tank capacity | Mandatory
| Radiator coolant & water mixure ratio | Vendor will mention the capacity of proposed ratio | Mandatory
| Recommended Fuel tank capacity (ltr) | Vendor will mention the capacity of proposed tank | Major
| In built circuit breacker capacity & originality | ABB/Schneider Italy original | Critical
D | Alternator Data
| Brand: | Leroy-Somer/ Stanford/MecAlte or or Equivalent | Critical
| Manufacturer: | UK/USA/ Germany/Italy/ France/ China/India/EU | Critical
| Country of origin: | UK/USA/Germany/Italy/France | Critical
| Model: | Vendor must mention as per OEM catalogue | Info
| Capacity: | Vendor must mention as per OEM catalogue | Major
| O/P current at full load: | Please mention the current, Air Cooled/water cooled, Insulation Class-H | Major
| Voltage Regulation mode | Auto | Critical
| Alternator Voltage Regulation, Steady State | ≤ ±1% | Critical
| Excitation Mode | Brushless, self-excited, self-regulated with efficiency of >95% | Major
| Phase & Wires | 3 Phase, 4 Wires | Major
| Protection Class | IP22/ IP23 | Major
| Number of Pole | Vendor must mention as per OEM catalogue | Major
| Power Factor | Vendor must mention as per OEM catalogue | Major
| Frequency | Vendor must mention as per OEM catalogue | Critical
| Output Voltage(V) 3-phase and 1-pgase | Vendor must mention as per OEM catalogue | Critical
| Output Current(A) | Vendor must mention as per OEM catalogue | Critical
E | Control Panel data
| Brand | Smartagan/ Deepsea/ ComAp, Woodward/Power Wizard/ equivalent etc. | Critical
| Manufacturer | Vendor must mention as per OEM catalogue | Critical
| Model | Vendor must mention as per OEM catalogue | Info
| Synchronizing facility | Must have synchronized facility | Critical
F | ATS with AMF
| 4P ACB rating | Vendor must mention as per OEM catalogue | Major
| Low voltage limit 3 Phase | Min 280V, Adjustable | Major
| High voltage limit 3 phase | Max 480V, Adjustable | Major
G | Sound attenuated canopy
| Canopy |  | Mandatory
| Sound Level @ 1 meter distance | 75 db(A) at our site environment w/o Reference | Critical
| Sound Level @ 1 meter distance will remain till _______Running Hour of DG. | 75 db (A) 5000 Hrs at our site environment w/o Reference | Critical
Without canopy/open type
| Sound Level @ 1 meter distance | db(A) value at our site environment w/o Reference [vendor will share dB(A)] | Critical
| Sound Level @ 1 meter distance will remain till _______Running Hour of DG. | db (A) value at 5000 Run Hrs at our site environment w/o Reference [vendor will share dB(A).] | Critical
H | Operating Ambient Temperature
| Recommended Operating Ambient Temperature (Manufacturer document must submit with offer) | 15-50°C | Critical
| Environment | The generator should be capable of operating in given site condition/situation | Major | [6 empty] | Carbon emission Data is necessary for IFC Audit
I | Physical Data
| Generator With canopy | DG Canopy should Fire resistive standard (min 2 hrs), should provide a certificate | Major
| i. Generator dimension LengthxWidthxHeight: In mm | Vendor must mention as per OEM catalogue | Critical
| ii. Generator Weight (In Kg) With canopy | Vendor must mention as per OEM catalogue | Major
Generator Without canopy
| i. Generator dimension LengthxWidthxHeight: In mm | Vendor must mention as per OEM catalogue | Major
| ii. Generator Weight (In Kg) without canopy | Vendor must mention as per OEM catalogue | Major
| Built in Fuel tank capacity (In liter) | Vendor will mention | Major
| Silencer type | Critical Grade, Critical grade means exhaust noise reduction from 25 dbA to 32 dbA | Critical
| Generator display | Vendor need to mention details display parameter | Major
| Fuel Tank display | Vendor need to mention details display parameter | Major
| Fuel Filter | Vendor to provide additional filer at Generator for incoming fuel | Critical
J | Operational Data
Fuel Consumption in liter per hour:
| i. At 110% load: | Vendor must mention as per OEM catalogue | Critical
| ii. At 100% load: | Vendor must mention as per OEM catalogue | Critical
| iii. At 75% load: | Vendor must mention as per OEM catalogue | Critical
| iv. At 50% load: | Vendor must mention as per OEM catalogue | Critical
| Generator set life time in hours | Vendor must mention as per OEM catalogue | Critical
| Continuous operation time at >75% Load (Recommended by manufacturer) | 12 Hrs/ Day (at least) | Critical
| Maximum overload utilization with duration | Vendor must mention max % of utilization with duration | Critical
| Monitoring | Inbuilt with RMS features & can be integrated with DCIM | Critical
| Top Overhauling period (in hours) | Vendor must mention as per OEM catalogue | Major
| Major Overhauling period (in hours) | Vendor must mention as per OEM catalogue | Major
| Preventive service period (in hours) | Vendor must mention as per OEM catalogue | Major
| Radiator service period (in month) | Vendor must mention as per OEM catalogue | Major
| Engine shutdown temperature level | Vendor must mention as per OEM catalogue | Critical
| Engine load factor in percentage | Vendor must mention as per OEM catalogue | Major
| De-rating factor above 40°C (open set) | Vendor must mention as per OEM catalogue | Major
| Anti-vibration pad: | Anti vibration pad under generator. | Critical
| Battery: | Industrial type, long life time battery for start genset and control panel. | Critical
| Earthing works: | Supplier to arrange required earth electrodes and risers with proper earth boring for new for generators as per site condition with OEM standrard | Major
| Equipment design Life time/End of Life (EoL) | Vendor must mention as per OEM catalogue | Critical
| End Of Service (EoS) | Vendor must mention as per OEM catalogue | Critical
| Generator warranty | Min 02 (Two) years full warranty including all spare parts. Vendor should mention the Year | Critical
| Annual Maintenance Contact (AMC) | 05 (Five) years after warranty period | Critical
| Radiator servcing | Free during warranty period | Major
| Quaterly/250 hours/Robi scheduled DG PMS | Free during warranty period | Critical
| DG performance will remain same during warranty period | Vendor must mention as per OEM catalogue | Critical
| Performance degradation after warranty (%) | Vendor will share % of degradation as per OEM | Critical
K | Others data
| Load test | Vendor to arrange load test at Robi site/supplier WH @110% dummy 1hr or as per spec, Live load ~75% to verify rated capacity. | Mandatory
| Delivery Lead Time | Please mention delivery lead time (From PO date) | Critical
| Installation Time | Please mention installation timeline after delivery | Major
| Software | Vendor to provide higher capacity Generator with free license | Critical
| Training | Vendor to provide training on operation, troubleshooting and maintenance at Robi premises or Supplier premises | Minor
| User Manual and product technical documents | Vendor to provide maintenance manual with product and Technical specification will provide with RFQ submission | Major
| Specification justification of products | Must be justified Through official website. Please mention the official web address | Minor
| Available space | Vendor to survey the site and comply the available space | Critical
| Authorization | Vendor will be authorized as dealer or agent of supplied product from manufacture company.(supporting document must be enclosed) | Minor
| DG/controller softwire handover | Vendor will provide updated licence version | Critical
| Specific type DG maintenance tools box | Vendor will provide tools box | Major
| Experience | Vendor will provide the experience of Supply and support document of higher capacity generator & synchronizing system | Info
| Telecom Experience of higher capacity Generator | Vendor to mention in their office letter head paper | Info
| Generator Synchronizing experience with O&M | Vendor to mention in their office letter head paper | Info
| Vendor logistic support | Vendor to mention in their office letter head paper | Info
| Vendor own experties team & equipment | Vendor to mention in their office letter head paper | Info
| Office set up | Vendor to mention in their office letter head paper | Info
| Others specifications | if any (please mention in details) | Info
| Spare parts gurantee | Vendor to mention in their office letter head paper | Info | [6 empty] | Vendor must ensure spare parts availability
| DG Minor & Major Overhauling guideline | Vendor to mention in their office letter head paper | Info | [6 empty] | Vendor must ensure minor overhauling duration
| Monitoring Protocol | SNMP/BACnet/Modbus | Critical
| Protocol Version | Vendor need to mention the protocol version like V2, V3 etc. | Critical
| Protocol file | Need to share the protocol file | Critical
| Cooling Type | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring | Critical