## NMS Spec
SL | Items | Descriptions: | Criticality | FC/PC/NC | Remarks if any (for PC or NC)
1 | Monitoring Protocol | SNMP/BACnet/Modbus | Critical
2 | Protocol Version | Vendor need to mention the protocol version like V2, V3 etc. | Critical
3 | Protocol file | Need to share the protocol file | Critical
4 | Cooling Type | Has to be smart and compatible with Power EMS/NMS/RMS for remote monitoring | Critical

## Substation
Substation Technical specification:
SL | Descriptions: | Criticality | FC/PC/NC | Remarks if any (for PC or NC)
1 | Standard and codes of practice | Mandatory
| Standard, approval and codes of practice applicable. | Mandatory
| Sub-Station (Distribution Transformer, 11/0.415KV) has been listed and proven to comply with any of the following internationally accredited body:- | Mandatory
| A) UL/ CE certified | Mandatory
| B) IEC standards/Equivalent | Mandatory
| C) VDE/DIN/Equivalent | Mandatory
2 | Design Requirements: | Mandatory
| The design shall be for complete Sub-Station (11/0.415KV) [capacity as per BoQ] | Mandatory
3 | DROPOUT FUSE: | Critical
| Rated Voltage (Nominal) : 11 KV | Critical
| Rated Maximum Voltage : 15 KV | Critical
| Rated Frequency : 50 Hz | Critical
| Rated Current (rms.) : 75 A | Critical
| Rated interrupting capacity : 10 KA | Critical
| Withstand Voltage : 35 KV (1 Min. Dry.) | Critical
| Withstand Voltage : 30 KA (10 Sec. Wet) | Critical
4 | Lightning Arrester (Technical Specification): | Critical
| Rated Voltage (RMS) : 9 KV | Critical
| Rated System Voltage : 12 KV | Critical
| Frequency : 50 Hz | Critical
| Minimum Spark Over (RMS) : 14 KV | Critical
| Maximum Spark Over (RMS) : 40 KV | Critical
| Withstand Voltage: | Critical
| - Wet. 10 sec : 24 KV | Critical
| - Dry. 1 min : 28 KV | Critical
| Discharge 33 KV (Crest) : 5 KA | Critical
| Impulse Current Withstand : 55 KA | Critical
5 | 11 KV H.T. SWITCHGEAR: | Mandatory
| Sheet steel clad (14 gage sheet), Birch gray color powder coating painting, free standing, floor mounting indoor HT Switchgear 11KV. 50Hz, three phase, 630A hard drawn electrolytic copper bus bar equipped with | Mandatory
| 1 No. 630 A, 50Hz, 11KV, 25KA TP V.C.B with auxiliary contacts, tripping and ON/OFF indicators (withdrawable). | Mandatory
| 1 No. 630 A, 50Hz, 11KV, 25KA TP MANUAL ISOLATOR | Mandatory
| IDMT Relay for over current, short circuit and earth fault protection (microprocessor base) | Mandatory
| 3 No’s Cast resin insulated double core CT 60/5/5A, type IS12C/equivalent | Mandatory
| Core 1 :15VA, Class 0,5 M5 | Mandatory
| Core 1 :15VA, Class 10 P10 | Mandatory
| 2 No’s Cast resin PTs, type, ZYE 10a/equivalent | Mandatory
| Ratio: 11000/110V, Burden 50(85) VA , Class: 05 (1) | Mandatory
| 1 No. TP MCB for PT Secondary Protection. | Mandatory
| 1 No. Voltmeter, range 0-15KV with Selector Switch | Mandatory
| 1 No. Ammeter, range 0-60A with Selector Switch | Mandatory
| 2 Nos. indicating Lamps ON/OFF. | Mandatory
| 1 No. Panel Heater. | Mandatory
Mandatory
| Note: | Mandatory
| V.C.B. country of origin of Germany/USA/UK/Italy with drive test certificate/ (ABB/Siemens/Schneider) | Mandatory
| C.T. P.T. brand Energy PAC/Seimens/Schneider | Mandatory
6 | Distribution Transformer: (11/0.415KV) | Critical
| 3 Phase oil immersed, naturally air cooled Transformer acc. to VDE/IEC/DIN standard with 3 HT Bushing and 4 LT Bushings arranged on tank top, conservator, oil level indicator, drain and filling valves, lifting lugs, bi-directional rollers, with first filling of oil Transformer including Off-load tap changer. | Critical
| Technical data: | Critical
| Rated Capacity : 100 KVA - 2500 KVA [as per BoQ] | Critical
| Rated Frequency : 50 Hz | Critical
| Rated Voltage: | Critical
| Primary : 11000V | Critical
| Secondary : 415 V | Critical
| Vector Group : DYN 11 | Critical
| Off-load tap changer : ± 2x 2.5 – 7.5% | Critical
| Ambient Temperature : 40 °C | Critical
| Temperature rise: | Critical
| - in Oil : 60°C (Max) | Critical
| - in Coil : 65°C (Min) | Critical
Critical
| Star Point brought | Critical
| Out & load-able up to : 100% | Critical
| Max. Service altitude : 1000 meters | Critical
| Installation : Indoor/Outdoor | Critical
| No Load Losses : 0.1% (approx) | Critical
| Full Load Losses : 1% (approx.) | Critical
| Impedance : 4 to 6 % (approx.) | Critical
Critical
| Accessories: | Critical
| - Silica gel breather | Critical
| - Thermometer | Critical
Critical
| Core -Japan/Europe/equivalent | Critical
| Oil- Hyrax/BP | Critical
| (Note: Preferable of Reputed Brand and vendor must have own manufacturing Factory. | Critical
7 | LT switchgear: | Mandatory
| Sheet Steel clad (14 gage sheet), Birch gray color powder coating painting, free standing, floor mounting type, 415V, 50Hz, indoor type Low Tension Switch gear with 3000A hard drawn copper bus-bars, TPN & E equipped with | Mandatory
| Incoming: | Mandatory
| ACB/MCCB with TP+N | Mandatory
Mandatory
| Outgoing: | Mandatory
| ACB/MCCB with TP+N | Mandatory
| Note: | Mandatory
| All breaker will be installed inside the LT switch gears and all MCCB/ACB will be made in Italy/France/India/China, supplier must provide drive test certificate and QC certificate for higher capacity ACB/MCCB | Mandatory
Mandatory
8 | Power Factor Improvement Plant: | Major
| Industrial Type | Major
| 16 stage | Major
| Capacity as per substation capacity | Major
| Origin of P.F.I Plant Components: | Major
| Capacitors: Ducati/Energia/Enerlux/Siemens/equivalent, Made in Europe/USA/Japan/China | Major
| Magnetic Contactor brand Togami/ telemechanic /Schneider Made in Japan/China/France/Europe | Major
| 12 stage Automatic P.F. Correction Relay: Made in Germany/UK/USA | Major
| CB: Siemens/ABB/Scheneider, Made in Germany/Italy/France/China | Major
| Note: MC, CB and capacitor bank will be fitted as per requirement and capacity & no of quantity may changed | Major
9 | Power Cables: | Major
| - HT Power cable (as per design), XLPE/NYSEYFGbY, BBS/BRB/SQ---quantity as per requirement | Major
| - Power cable, as per design, NYY FR cable, BBS/BRB/SQ qty-as per requirement | Major
| - Grounding cable, as per BNBC guideline , green—BBS/BRB—approx.. 300 mtr / as per requirement | Major
| 11 KV Line constructions from 11kv REB feeder to Robi premise with necessary fittings & fixing and 11KV H-pole construction for Isolator installation with necessary fitting & fixing. | Major
| Approval for H.T. Metering issue | Major
| Approval from Electric Licensing Board (ELB) authority | Major
10 | SAFETY ISSUES FOR ELECTRICAL/OTHERS CONTRACTORS: | Major
Major
| They should practice: | Major
Major
| 1. They should use rubber shoe/safety shoe during work | Major
| 2. They should not work on live wire, even on work safety gloves is must. | Major
| 3. Helmet is mandatory during work | Major
| 4. Safety belt during ladder work is must | Major
| 5. Enough light during work at work place | Major
11 | Others information: | Mandatory
| Size (LxDxH) of the HT/LT/PFI cabinet must be approved by Robi / Robi Technical team before construction. | Mandatory
| Quality & Finishing of Frame must be approved by Robi/Robi Technical Team | Mandatory
| All equipment must be tested by Robi/Robi engineer at Vendors Lab before delivery | Mandatory
| VCB, ACB, MCCB Factory Test Report/drive test certificate must be included along with the Commissioning Report | Mandatory
| Earth Leakage /No Load/Full Load test for TX-former at Vendor Lab or any reputed test lab is mandatory before delivery. | Mandatory
| All Test report must be incorporated along with Commissioning report | Mandatory
12 | Warranty of the complete product Minimum 2 years warranty | Mandatory
13 | End of Life of complete product (Vendor will mention) | Critical
14 | Rollout or Installation time, Max 4 weeks | Critical
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________

## Electrical
Electrical Technical specification:
SL | Main items | Descriptions: | Criticality | FC/PC/NC | Remarks if any (for PC or NC)
1 | DB’s & PDU’s (raw power) | The normal PDU’s for light & utilities, HVAC system should have built in STS/ ATS & supports two input power feed | Mandatory
- Standard: BS/IEC/EN 60439-1 form 1, 2, 3 & 4 or updated or any relevant standard
- Environment: EN 60439-1:1999 section 6.1.1.1 or updated or any relevant standard
There should be 20% extra spare breakers as an spare for future need
2 | Color Coding | Standard Color coding for RYBN & Yellow Green (Ground) | Mandatory
3 | Redundancy | Must comply standards for power feed | Mandatory
4 | Compatibility | Modular, Scalable & Flexible | Critical
5 | Grounding | < 1 Ohm | Mandatory
6 | Common mode noise | <1% of phase to neutral value | Critical
7 | THDi | ≤ 5% | Mandatory
8 | Voltage | 400V +/- 10% | Major
9 | Frequency | 50Hz +/- 5% | Mandatory
10 | Load imbalance | Power load imbalance must be less than 10% between phases | Critical
11 | Reference Standard Electrical | EN, IEC or relevant standard | Mandatory
12 | Earthing | MIE –REBT, EN, ETSI or updated or any relevant standard | Mandatory
13 | EMF (Electro-Magnetic Fields) | EN or any relevant standard | Major
14 | Surge Protection | Each Distribution system irrespective of its size and capacity must be equipped with surge protection system as per standard/ best practice | Critical
15 | Warranty for all product | Minimum 2 years | High Critical
16 | End of Life of all product | Vendor will mention | Critical
17 | Rollout or Installation time | Max 4 weeks | Critical
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________

## Lighting and others
Lighting and accessories Technical specification:
SL | Main items | Descriptions | Criticality | FC/PC/NC | Remarks if any (for PC or NC)
1 | Light & Utilities | Should comply the standard EN12464-1 for light & lighting works as well as ANSI/ TIA -942 or any standard require | Mandatory
2 | Illumination Level | The illumination level inside the DC room must be as per below. | Major
- Computer Room : 600 Lux
- Staging & Service Corridor : 500 Lux
- Electrical & AC/DC Rom : 300 Lux
- Other service area : 200 Lux
3 | Light Types | The Light must be spark free, LED light & SMD Type | Minor
4 | Location & power supply | The lights must be available in all aisle (Hot & Cold), corridor, rooms & premises. | Major
The power supply should be raw power
5 | Outdoor Light | - The outdoor premises must be equipped with sufficient luminaries | Major
- The light should be IP55/56 protected outdoor type light
6 | Emergency Light | - The light categories should be as per BS standard | Major
-The Lighting system should be as per BS/EN standard
- The minimum value of light intensity for emergency should be 15 Lux
- The light must be visible during Fire or smoke
7 | Surge Reduction Filter(SRF) | Model: SRF3250N, SRF3500N Brand: Erico, SRF N-SERIES | Mandatory
8 | Power cable Ladder | 16 Gauge MS/GI sheet, Special Power Coated, Nut & Bolts has to be SS. | Mandatory
9 | Roxtec | 6x2 with Sealing Gasket & mounting Hardware, Frame: KFO RM40-18 no, RM30-6 no, RM20 w40-4, RM15 w40-6; Including Roxtec Wedges-2 no, Roxtec Stayplates-12 no, Roxtec Lubricant/Roxtec Assembly Gel-1 no Brand: Walmax/Equivalent | Mandatory
6x1 with Sealing Gasket & mounting Hardware, Frame: KFO RM40-6 no, RM30-6 no, RM20 w40-3, RM15 w40-3; Including Roxtec Wedges-1 no, Roxtec Stayplates-12 no, Roxtec Lubricant/Roxtec Assembly Gel-1 no Brand: Walmax/Equivalent
10 | Lightning Arrester (DYNASPHERE type) | Complete DYNASPHERE type lightning arrester excluding grounding cable and including grounding PIT and accessories where need to be included lightning event counter. Coverage system: telecom tower, switch room, electrical system, Generator, substation etc and around 40 decimal land of each site | Mandatory
Brand: ABB/Erico/Schneider/Simillar
Model
Origin and Manufacture
Standard: EN/IEC 62305 or updated
Coverage radious (r) (meter) of each system (As per NF C 17-102)
Height of Protection (meter)
Counter limit in quantity
Waveshape (μs)
di/dt (max) (kA/μs)
Peak Current (kA)
Minimum Current (kA)
Class of Lightning protection system (Class I/II/III/IV)
11 | Harmonics elimination device (Integrate in series/parallel with Power system) | Brand Name | Mandatory
IEEE Standard 519 or updated
Elimination harmonics- 3rd, 5th and above. Please mention the details
Please mention, Total Harmonics distortion in % at LT side after elimination (minimum ≤ 5%)
Feature need to be included: Reduced Neutral Current, Reduced Neutral-Ground Voltage, Reduced Peak Phase Current, Reduced Average Phase Current, Reduced Total Harmonic Distortion of Current (THDI), Reduced Total Harmonic Distortion of Voltage (THDV), Reduced Apparatus and Circuit Losses, Reduced Overheating, Increased True Power Factor, Improved Protective Device Performance, Reduced Errors in Power Metering, Decreased Apparatus Vibration, Improves Phase Current Balance, Improves Phase Voltage Balance, Carry Through Single-Phase Outage, Decreased Telephone Interference Factor, Stand-Alone Solution
Please mention the display parameter
Country of origin:
Manufacturing country:
12 | Harmonics Blocking Plate (affixed on a power cable) | Site survey, drawing analysis, financial analysis, installation, and commissioning of Harmonics reduction energy saving plates | Mandatory
Service provider will ensure the installation and proper functionality of the plate.
Savings output must be minimum 3% on current electricity consumption with 01 year performance guaranty.
KPI: Savings minimum 3% on current electricity consumption= 100%
13 | Sanction load | Has to comply the guideline of Bangladesh power authority like ELB, BPDB, REB etc | Major
14 | Warranty for all product | Minimum 2 years | High Critical
15 | End of Life of all product | Vendor will mention | Critical
16 | Rollout or Installation time | Max 4 weeks | Critical
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________

## AFPS
A | AFPS Technical specification:
Item | Title | Technical Specifications / Recommendations | Importance | FC/PC/NC | Remarks if any (for PC or NC)
1 | Fire Detection & Suppression System
2 | Standard | - Should comply with National & Building Code | Mandatory
3 |  | - NFPA 2001/ ISO 14520 or updated | Mandatory
4 | Detection | Detection system should be Smoke and Heat detection based | Critical
5 | Brand | As per Technical BoQ | Critical
6 | Origin | As per Technical BoQ | Critical
7 | Safety | - Should be Environment friendly | Critical
8 |  | - No observed Adverse Effect Level (NOAEL) to humans & equipments | Critical
9 | Fire Suppression | Novec 1230, NAF S 125 and FM200 | Mandatory
10 | System Operation | Fully automatic as well as manual provision with CE/ UP certification | Major
11 | Outside Premises | There should have fire suppression/extinguishing system for outside premises of the datacenter building to protect | Critical
12 | Portable Cylinders (ABC) | For Fuel storage area, outdoor power station, generator room | Major
13 | Signage & Safety | Exit/ Emergency signs to be located at every escape door, pathways leading to doors and must be visible from all areas | Critical
14 | Alarm Bell | There should be alarm bell in case of fire detection | Critical
15 | Hold Time | The hold time of gas concentration after release must be ≥ 10 minutes at the highest electrical point inside datacenter | Critical
16 | Discharge point Clearance | Discharge Nozzle should be unobstructed | Critical
17 |  | - Minimum of 1.5 Mtr in Horizontal plane | Critical
18 |  | - Minimum of 400mm in vertical plane | Critical
19 | Reference Standard |  | Major
20 | Fire protection | NFPA-75, NFPA-2--1 or updated | Mandatory
21 | Operation and Maintanence data |  | Major
22 | Equipment design Life time/End of Life (EoL) | As per Original Equipment Mmanufacturere | Critical
23 | End Of Service (EoS) | As per Original Equipment Mmanufacturere | Critical
24 | Generator warranty | 02 (Two) years full warranty including all spare parts. | Mandatory
25 | Annual Maintenance contact | 03 (Three) years after warranty period | Critical
26 | AFPS System | Hydraulic Calculation | Critical
27 | AFPS System | Fire Suppuration Layout drawing e2e Zone wise | Critical
28 | AFPS System | Full System Layout Drawing | Critical
29 | Detection | Smoke and Heat detection system should be standard and good quality | Critical
30 | Pressure Check | Should ensure Zone wise Connected Steel Pipes Hydraulic Pressure Test based on Zone wise connected Cylinder Gas Pressure | Critical
31 | Cylinder Pressure and Gas weight | Should ensure each Cylinder Pressure and Gas weight | Critical
32 | AFPS System | Ensure Cylinder test report | Critical
33 | AFPS System | Smoke Sensor, Heat Sensor, Cylinder test report | Critical
34 | AFPS System | Ensure Valve Test report | Critical
35 | Cable | All Cables should NYYFRLS | Critical
36 | Pipe | All Fire suppuration Pipe should standard and reputed brand | Critical
B | AFPS (VESDA Based) Technical specification:
1 | Standard | - Should comply with National & Building Code | Mandatory
2 |  | - NFPA 2001/ ISO 14520 or updated | Major
3 | Detection | Detection system should be VESDA (Very Early smoke detection apparatus). | Mandatory
4 | Smoke Detector | Ionization detectors | Mandatory
5 | Safety | - Should be Environment friendly | Mandatory
6 |  | - No observed Adverse Effect Level (NOAEL) to humans & equipments | Mandatory
7 | Fire Suppression | Novec -1230 | Mandatory
8 | Hydrogen detecting and discharging system | Automatic | Mandatory
9 | System Operation | Fully automatic as well as manual provision with CE/ UP certification | Major
10 | Outside Premises | There should have fire suppression/extinguishing system for outside premises of the datacenter building to protect | Mandatory
11 | Portable Cylinders (ABC) | For Fuel storage area, outdoor power station, generator room | Major
12 | Signage & Safety | Exit/ Emergency signs to be located at every escape door, pathways leading to doors and must be visible from all areas | Mandatory
13 | Alarm Bell | There should be alarm bell in case of fire detection | Mandatory
14 | Hold Time | The hold time of gas concentration after release must be ≥ 10 minutes at the highest electrical point inside datacenter | Mandatory
15 | Discharge point Clearance | Discharge Nozzle should be unobstructed | Mandatory
16 |  | - Minimum of 1.5 Mtr in Horizontal plane | Mandatory
17 |  | - Minimum of 400mm in vertical plane | Mandatory
18 | Reference Standard
19 | Fire protection | NFPA-2001 or updated | Info
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________

## Civil Design
Civil Design Technical specification:
S/N | Items | Criteria | FC/PC/NC | Remarks if any (for PC or NC)
1 | Survey | Need to prepare
2 | Soil Test & report submission | Need to prepare
3 | Arch & Structural design | Need to prepare
4 | Electrical Wiring & Lighting Design | Need to prepare
5 | Grounding design | Need to prepare
6 | Plumbing Design | Need to prepare
7 | FPS & FDS | Need to prepare
8 | Approval from City Corporation/Paurashova/Union Paurashova | Agreed/Dis-agreed
9 | NoC from the Department of Environment | Agreed/Dis-agreed
10 | NoC from the Fire Service and Civil Defense | Agreed/Dis-agreed
11 | NoC from the RHD | Agreed/Dis-agreed
12 | Structural Design vetted by BUET | Agreed/Dis-agreed
13 | Architectural Design vetted by BUET | Need to prepare
14 | Structural Working Drawings Vetted by BUET | Need to prepare
15 | BoQ Preparation for Dismantle of existing buildings | Need to prepare
16 | Detailed e2e design BoQ | Need to prepare
Time line
17 | Survey and soil test report | 15 days from PO
18 | All design report | 15 days from PO
19 | BUET Approval | 15 days from PO
20 | NOC from Govt Authority | 30 days from PO
General
21 | Experience of Firm | Minimum 5 years
22 | Reputation/Standard of Firm | Minimum 5 high volume work
23 | Experience in Telekom sector | Minimum 2 high volume work
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________

## DG Service
Generatorn Service Technical specification:
SL | Particulars | Specification | Criticality | FC/PC/NC | Remarks if any (for PC or NC)
1 | Working experience | Available work experinec on any brand/type of DG (Example: Catterpiller, Kohler, Tempest, Forestcity, Powerlink, Pramac, FG Wilson, Cummins, Gucbir, Electro etc) | Critical
2 | Roll back plan | During execution, vendor need to be prepared details roll back plan with proper safety security measure | Critical
3 | ATS For DG | Schenider/ABB 4P Breaker with OEM certificate | Major
4 | DG accessories | DG accessories has to be sourcing from original equipment manufacturer | Major
5 | Earthing works | Supplier to arrange required earth electrodes and risers with proper earth boring for new for generators as per site condition with BNBC guideline. Grounding value should be less than 1 ohm | Major
6 | Sound attenuated canopy: Sound Level @ 1 meter distance | 75 db(A) at our site environment w/o Reference | Critical
7 | Built in Fuel tank capacity (In liter) | As per scope of work and SOR | Major
8 | Silencer type | Critical Grade | Critical
9 | Fuel Tank display | Digital display with consumption | Major
10 | Fuel Filter | Fuel filer at Generator for incoming fuel | Major
11 | Load test | Load test may require to check the functionality as per respective DG OEM guideline | Major
12 | Tools | Proper tools with data logger availability for any analysis | Major
13 | Experience | Vendor will provide the experience of Supply and support document of higher capacity generator servicing, relocation & synchronizing system | Major
14 | Telecom Experience of higher capacity Generator | Vendor to mention in their office letter head paper | Info
15 | Generator Synchronizing experience with O&M | Vendor to mention in their office letter head paper | Info
16 | Vendor logistic support | Vendor to mention in their office letter head paper | Info
17 | Vendor own experties team & equipment | Vendor to mention in their office letter head paper | Info
18 | Office set up | Vendor to mention in their office letter head paper | Info
19 | Others specifications | if any (please mention in details) | Info
20 | DG Minor & Major Overhauling | Guideline and experience | Info
21 | Spare parts warranty | At least one year (more is preferable) | Critical
22 | Consumable items warranty | Six months | Critical
23 | Service Warranty | 3 months from PAT, FoC under warranty spare & old spare will supply by Robi | Critical
24 | Fall Back | Supplier must be ensure to previous/existing DG will be activated/Live as per initial condition without any commercial impact | Critical
Note:
• Fully Compliant (FC) shall be understood as: Bidder fully complies with the contract clause / requirement; Supplier cannot incorporate any condition/contingencies.
• Partially -Compliant (PC) shall be understood as: Bidder does not complies with the contract clause / Robi requirement fully
• Non-Compliant (NC) shall be understood as: Bidder does not complies with the contract clause / requirement
• If no statement of compliance has been given to a certain requirement, then the requirement will be considered as "Not Complied" to by the Bidder.
• “Fully Compliant” Sections and Sub-sections shall not be negotiated upon.
• The Bidder is requested to propose an alternative text for all Non-Compliant (NC) articles in the contractual parts of RFQ.
| Signature | :____________________________________
| Name of the Signatory | :____________________________________
| Desigtation of the Signatory | :____________________________________
| Name of the Company | :____________________________________
| Date | :____________________________________